## DAILY A CHECK LIST
DIESEL GENERATOR DAILY 'A' CHECK LOG SHEET
|  |  |  | SITE NAME | [9 empty] | ENGINEERING & OPERATIONS SOLUTIONS GROUP | [13 empty] | CHK NO: E&OS/DG/001
|  |  |  | LOCATION |  |  | Need Master list of the location / Sub locaiton / Zone | [20 empty] | REV NO: 00 (Help us with the actual Rev no:)
|  |  |  | CAPACITY |  |  | Master list required of the existing capacity | [20 empty] | RELEASE DATE: 25/08/2010
Sl.No | Activities |  | Spec | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
Cleaning
1 | Clean the Engine, Fuel & Air hoses |  | Free from dirt | ?Query What is to be captured here, Yes / No / NA, etc…
2 | Clean the alternator |  | Free from dirt | ?Query What is to be captured here, Yes / No / NA, etc…
3 | Clean the cable terminal box |  | Free from dirt | ?Query What is to be captured here, Yes / No / NA, etc…
4 | Clean the air & fuel filters ( externally ) |  | Free from dirt | ?Query What is to be captured here, Yes / No / NA, etc…
5 | Clean the radiator & coolant pipe lines |  | Free from dirt | ?Query What is to be captured here, Yes / No / NA, etc…
6 | Clean the batteries & cables |  | Free from dirt | ?Query What is to be captured here, Yes / No / NA, etc…
Inspection
Sl.No | Station No | Activities | Spec
1 | 1 & 2 | Check the battery voltage | > 23vdc and < 25vdc | ?Query What is to be captured here, Yes / No / NA, etc…
2 | 1 | Check the specific gravity of batteries | > 1.15 & < 1.3 | ?Query What is to be captured here, Yes / No / NA, etc…
3 | 1 | Check the Battery Electrolyte Level | 15mm above the Plates | ?Query What is to be captured here, Yes / No / NA, etc…
4 | 1 & 3 | Check all hoses, pipes for any leakages & arrest it immediately | Free from Oil & water tracings | ?Query What is to be captured here, Yes / No / NA, etc…
5 | 1 & 3 | Check the condition of Air inlet restriction Indicator | Up to Service Level | ?Query What is to be captured here, Yes / No / NA, etc…
6 | 1 | Check the Engine lubricating Oil level | Between L & H | ?Query What is to be captured here, Yes / No / NA, etc…
7 | 1 & 3 | Check the abnormal noise & vibration while taking trial run | Should be working normal | ?Query What is to be captured here, Yes / No / NA, etc…
8 | 1 | Check engine starter motor cable terminals for any looseness | No loose | ?Query What is to be captured here, Yes / No / NA, etc…
9 | 2 | Check the engine control panel & display working condition | Should be working | ?Query What is to be captured here, Yes / No / NA, etc…
10 | 2 | Ensure selector switch position in control panel is in Auto mode | Always in Auto position | ?Query What is to be captured here, Yes / No / NA, etc…
11 | 3 | Check the condition of radiator fan Belt and its tension | Free from crack or Damage | ?Query What is to be captured here, Yes / No / NA, etc…
12 | 3 | Drain water from fuel water separator through drain valve | Till diesel comes | ?Query What is to be captured here, Yes / No / NA, etc…
13 | Radiator Top | Check the Radiator water & coolant level | Up to the brim | ?Query What is to be captured here, Yes / No / NA, etc…
14 | Daily tank | Check the Diesel level in the daily fuel tank | > 75 % of tank | ?Query What is to be captured here, Yes / No / NA, etc…
Sign of Technician |  |  |  | Employee Mater list (Employee Name, Employee code no: (auto populated based on employee name), Employee Designation (auto populated based on employee name))
Sign of Supervisor |  |  |  | Employee Mater list (Employee Name, Employee code no: (auto populated based on employee name), Employee Designation (auto populated based on employee name))

## DAILY DG OPERATION LOG SHEET
MONTH:
DAILY LOG SHEET FOR DIESEL GENERATOR
|  |  |  | ENGINEERING & OPERATIONS SOLUTIONS GROUP | [5 empty] | SITE NAME |  |  |  |  | CHK NO: E&OS/DG/002
[10 empty] | LOCATION |  | Need Master list of the location / Sub locaiton / Zone |  |  | REV NO: 00 | (Help us with the actual Rev no:)
[10 empty] | CAPACITY |  | Master list required of the existing capacity |  |  | RELEASE DATE: 25/08/2010
DATE | ON TIME | OFF TIME | Total Run Hrs | VOLTAGE | LOAD CURRENT AMPS. |  |  | FREQ | KW | OPENING READING | CLOSING REEDING | UNIT GENERATED (KWH) | FUEL |  | FUEL CONSUMED ( LTRS) | FUEL ADDED | AS ON DATE | UNIT GEN. PER LTR | TECH. SIGN
[5 empty] | R | Y | B |  |  | KWH | KWH |  | OPEN. LEVEL | CLOSE LEVEL |  |  | STOCK LVL
1 | ?AM / PM or HH:MM | ?AM / PM or HH:MM | Formula | ? Unit pls |  |  |  | ? Frequency Master |  |  |  |  | ? Unit pls | ? Unit pls |  | ? Unit pls | ? LVL??? |  | Employee Mater list (Employee Name, Employee code no: (auto populated based on employee name), Employee Designation (auto populated based on employee name))
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31

## DG MONTHLY CHECK LIST
MONTHLY CHECKLIST FOR DIESEL GENERATOR
|  | ENGINEERING & OPERATIONS SOLUTIONS GROUP | [5 empty] | SITE NAME |  |  | CHK NO: E&OS/DG/003
[8 empty] | LOCATION | Need Master list of the location / Sub locaiton / Zone |  | REV NO: 00 (Help us with the actual Rev no:)
[8 empty] | CAPACITY | Master list required of the existing capacity |  | RELEASE DATE: 25/08/2010
SL.NO | DESCRIPTION | JAN | FEB | MAR | APR | MAY | JUNE | JULY | AUG | SEP | OCT | NOV | DEC
1 | Check Air intake piping | JAN: ?Query What is to be captured here, Yes / No / NA, etc…
2 | Check the Radiator water & coolant level | JAN: ?Query What is to be captured here, Yes / No / NA, etc…
3 | Check fuel water separator | JAN: ?Query What is to be captured here, Yes / No / NA, etc…
4 | Check Engine lubricating oil filter | JAN: ?Query What is to be captured here, Yes / No / NA, etc…
5 | Check for leaks or cracks in fuel line | JAN: ?Query What is to be captured here, Yes / No / NA, etc…
6 | Check the battery voltage | JAN: ?Query What is to be captured here, Yes / No / NA, etc…
7 | Check the level of distilled water & specific gravity | JAN: ?Query What is to be captured here, Yes / No / NA, etc…
8 | Check air filters condition and clean if necessary | JAN: ?Query What is to be captured here, Yes / No / NA, etc…
9 | Check and correct leaks on oil and water in circuit | JAN: ?Query What is to be captured here, Yes / No / NA, etc…
10 | Check the condition of radiator fan Belt and its tension | JAN: ?Query What is to be captured here, Yes / No / NA, etc…
11 | Check the Engine lubricating Oil level | JAN: ?Query What is to be captured here, Yes / No / NA, etc…
12 | Check engine starter motor cable terminals for any looseness | JAN: ?Query What is to be captured here, Yes / No / NA, etc…
13 | Drain water from fuel water separator through drain valve | JAN: ?Query What is to be captured here, Yes / No / NA, etc…
14 | Carry the Load test of DG (record the parameters in DG log sheet) | JAN: ?Query What is to be captured here, Yes / No / NA, etc…
Sign of Technician |  | JAN: Employee Mater list (Employee Name, Employee code no: (auto populated based on employee name), Employee Designation (auto populated based on employee name))
Sign of Engineer |  | JAN: Employee Mater list (Employee Name, Employee code no: (auto populated based on employee name), Employee Designation (auto populated based on employee name))

## HALF YEARLY CHECK LIST
DATE:
HALFYEARLY CHECKLIST OR B-CHECK FOR DIESEL GENERATOR
ENGINEERING & OPERATIONS SOLUTIONS GROUP |  | SITE NAME |  | CHK NO: E&OS/DG/004
|  | LOCATION | Need Master list of the location / Sub locaiton / Zone | REV NO: 00 (Help us with the actual Rev no:)
|  | CAPACITY | Master list required of the existing capacity | RELEASE DATE: 25/08/2010
SL.NO | DESCRIPTION | STATUS | REMARKS
1 | Check coolant inhibitor, Add coolant if necessary | ?Query What is to be captured here, Yes / No / NA, etc…
2 | Check fuel water separator | ?Query What is to be captured here, Yes / No / NA, etc…
3 | Check for leaks or cracks in fuel line | ?Query What is to be captured here, Yes / No / NA, etc…
4 | Check the battery voltage | ?Query What is to be captured here, Yes / No / NA, etc…
5 | Check the level of distilled water & specific gravity | ?Query What is to be captured here, Yes / No / NA, etc…
6 | Check air filters condition and clean if necessary | ?Query What is to be captured here, Yes / No / NA, etc…
7 | Check and correct leaks on oil and water in circuit | ?Query What is to be captured here, Yes / No / NA, etc…
8 | Check the condition of radiator fan Belt and its tension | ?Query What is to be captured here, Yes / No / NA, etc…
9 | Check engine starter motor cable terminals for any looseness | ?Query What is to be captured here, Yes / No / NA, etc…
10 | Drain water from fuel water separator through drain valve | ?Query What is to be captured here, Yes / No / NA, etc…
11 | Check Heat exchanger Zinc Plugs | ?Query What is to be captured here, Yes / No / NA, etc…
12 | Lubricate ball joints of the throttle linkage of Hyd. Governor | ?Query What is to be captured here, Yes / No / NA, etc…
13 | Check the governor Oil | ?Query What is to be captured here, Yes / No / NA, etc…
14 | Check the Aneroid | ?Query What is to be captured here, Yes / No / NA, etc…
15 | Clean fuel pump inlet screen | ?Query What is to be captured here, Yes / No / NA, etc…
16 | Change the lubricating oil and filters ( Fuel & Oil ) | ?Query What is to be captured here, Yes / No / NA, etc…
17 | Check Crankcase breather tube | ?Query What is to be captured here, Yes / No / NA, etc…
18 | Remove and install Coolant Filter | ?Query What is to be captured here, Yes / No / NA, etc…
19 | Check operation of Fan cooling | ?Query What is to be captured here, Yes / No / NA, etc…
20 | Carry the Load test of DG (record the parameters in DG log sheet) | ?Query What is to be captured here, Yes / No / NA, etc…
Sign of Technician |  | Employee Mater list (Employee Name, Employee code no: (auto populated based on employee name), Employee Designation (auto populated based on employee name))
Sign of Engineer |  | Employee Mater list (Employee Name, Employee code no: (auto populated based on employee name), Employee Designation (auto populated based on employee name))

## YEARLY CHECKLIST
YEARLY CHECKLIST OR 'C' - CHECK FOR DIESEL GENERATOR
ENGINEERING & OPERATIONS SOLUTIONS GROUP |  | SITE NAME |  | CHK NO: E&OS/DG/005
|  | LOCATION | Need Master list of the location / Sub locaiton / Zone | REV NO: 00 (Help us with the actual Rev no:)
|  | CAPACITY | Master list required of the existing capacity | RELEASE DATE: 25/08/2010
1 | Check coolant inhibitor, Add coolant if necessary | ?Query What is to be captured here, Yes / No / NA, etc…
2 | Checking and recording of end clearance of critical components such as Crankshaft, acc drive, turbo charges, water pump etc | ?Query What is to be captured here, Yes / No / NA, etc…
3 | Check for leaks or cracks in fuel line | ?Query What is to be captured here, Yes / No / NA, etc…
4 | Check the battery voltage | ?Query What is to be captured here, Yes / No / NA, etc…
5 | Check the level of distilled water & specific gravity | ?Query What is to be captured here, Yes / No / NA, etc…
5 | Check air filters condition and clean if necessary | ?Query What is to be captured here, Yes / No / NA, etc…
6 | Check and correct leaks on oil and water in circuit | ?Query What is to be captured here, Yes / No / NA, etc…
7 | Check the condition of radiator fan Belt and its tension | ?Query What is to be captured here, Yes / No / NA, etc…
8 | Check engine starter motor cable terminals for any looseness | ?Query What is to be captured here, Yes / No / NA, etc…
9 | Drain water from fuel water separator through drain valve | ?Query What is to be captured here, Yes / No / NA, etc…
10 | Check Heat exchanger Zinc Plugs | ?Query What is to be captured here, Yes / No / NA, etc…
11 | Lubricate ball joints of the throttle linkage of Hyd. Governor | ?Query What is to be captured here, Yes / No / NA, etc…
12 | Check the governor Oil | ?Query What is to be captured here, Yes / No / NA, etc…
13 | Check Aneroid adjustment | ?Query What is to be captured here, Yes / No / NA, etc…
14 | Replace Aneroid Breather | ?Query What is to be captured here, Yes / No / NA, etc…
15 | Clean fuel pump inlet screen | ?Query What is to be captured here, Yes / No / NA, etc…
16 | Change the lubricating oil and filters ( Fuel & Oil ) | ?Query What is to be captured here, Yes / No / NA, etc…
17 | Check Crankcase breather tube | ?Query What is to be captured here, Yes / No / NA, etc…
18 | Remove and install Coolant Filter | ?Query What is to be captured here, Yes / No / NA, etc…
19 | Check operation of Fan cooling | ?Query What is to be captured here, Yes / No / NA, etc…
20 | Clean the fuel tank from Inside. | ?Query What is to be captured here, Yes / No / NA, etc…
21 | Clean the Radiator / charge the air cooler externally | ?Query What is to be captured here, Yes / No / NA, etc…
22 | Inspect parts like Alternator / starter etc. | ?Query What is to be captured here, Yes / No / NA, etc…
23 | Checking of alignment of alternator | ?Query What is to be captured here, Yes / No / NA, etc…
24 | Check Alternator insulation resistance (with Megger) | ?Query What is to be captured here, Yes / No / NA, etc…
25 | Check and replace gaskets / oil Seals ,O ring if necessary | ?Query What is to be captured here, Yes / No / NA, etc…
26 | Carry the Load test of DG (record the parameters in DG log sheet) | ?Query What is to be captured here, Yes / No / NA, etc…
27 | Check the air cleaner / Evacuator valve, Change if required. | ?Query What is to be captured here, Yes / No / NA, etc…
Sign of Technician |  | Employee Mater list (Employee Name, Employee code no: (auto populated based on employee name), Employee Designation (auto populated based on employee name))
Sign of Engineer |  | Employee Mater list (Employee Name, Employee code no: (auto populated based on employee name), Employee Designation (auto populated based on employee name))